## Engine Health Check up
HEALTH CHECK - UP
Rig | Engine Application | Engine Make | Engine Details | Previous Health Check-up | Last Health Check -up | Problem | ACTION | Overhauling Details
GTC 50-01 | Carrier engine (Spare ) | CAT | Model : C-9 SR No : JSC01354 |  | 05/06/2025 | 1. According to health Check-Up, there is no fault in Engine | 1. Next Health Check-up is planned on March - 2026
| Mud pump engine | Cummins | Model : KTA-1150-C SR No : 25337851 | 28/08/2025 | 11/03/2026 | 1. Injector need to be Repaired 2. Hoses need to be Replaced 3.11/03/2026 - Inspection & testing has been done tested and found ok. | 1. 31/12/25 - Injector & pump calibration done & fitment done 2. Next Health Check-up is planned on July - 2026
| DG Set - 1 (125 KVA) | Supernova | Model : SVE125 SR No : E622CDJC204733G | 2025-03-10 | 27/11/25 | 1. All Engine Hose pipe Required 2. Fan belt Required 3. Diesel Inlet & outlet Pipe Required. 4. AVM Pad Required 4Nos. 5. Feed Pump Service Required. 6. As per Running Hours F.I.Pump & Nozzle Service & Calibration Required. 7. Engine Running More then 11000 Hours Run As per Customer data Shit So As per Running Hours Engine Overhauling required. | 1.Once D.G -2 is ready will proceed further.
| DG Set - 2 (125 KVA) | Supernova | Model : SVE125 SR No : E622CDJE215149G | 27/11/25 | 05/03/25 (Overhauled by Karnavati) |  | 1. 05/03/2026 - Top Overhauling Completed by Karnavati 2. 05/03/2026 - Fuel Pump & Injector Calibration Completed 3. 05/03/2026 - New Radiator Installed 4. 30/03/2026 - TPI Accepeted & found Ok 5. Next Health Check-up is planned on July - 2026 | 05/03/25 (Overhauled by Karnavati)
| DG Set- 3 (15 KVA TOWER LIGHT) | Ashok Leyland | Model : AL2CDG1 SR No : KDEM205220 | 19/05/2025 |  | 1. main switch not Working 2. Required Engine radiator service 3. Air filter need to be Replaced 4. slightly Leakage from fuel pump | 1. All the point have been rectified & resolved (Replaced a MCB, Serviced a Radiator, Not Found any Leakage from fuel pump)
GTC 50-02 | Carrier engine (Original 50-01) | CAT | Model : C-9 SR No : JSC08784 | 22/01/2026 | 02/04/2026 | 1. Fuel line NRV need to be replace. 2. 21/1/2026 - Fuel pump need to be calibrate 3. Oil filter housing body need to be replace | 1. NRV replce from akram bhai workshops C9 engine. 2. Fuel pump send to vendor for calibration 3. Oil filter housing replace from akram bhai workshop c9 engine
| Mud Pump | CAT | Model : C-15 SR No : BEM00178 | 07/06/2025 | 11/03/2026 | 1. 11/03/2026 - General check and "C" done 2. Radiator need to be replace, Head gasket 3. Fuel Injector need to be calibrate | 1. Mud Pump Radiator replaced
| DG Set -1 (125 KVA) | Cummins | Model : 6BTAA5.9-G3 SR No : P84089932 | 21/01/2026 | 2026-06-02 | 1. coolant temperature sensor need to be replace 2. Fuel pump & injector need to be calibrate 3. Fuel relay faulty 4. fan tensioner 5. Flywheel need to be replace | 1.14/02/2026 - fuel pump and injector sent for calibration. 2.21/02/2026 - Fuel pump and injector calibration done tested and found ok. 3. 30/04/2026 - Fly wheel ring replaced tested & Found ok. 4.01/05/2026 - Diesel tank cleaned
| DG Set - 2 (125 KVA ) | Cummins | Model : 6BTAA5.9-G3 SR No : P84089603 | 21/01/2026 | 2026-06-02 | 1. Faulty relay & fuel solenoid 2. Fuel pump & Injector need to be calibrate | 1.27/02/2026 - fuel pump and injector fitted tested & found ok. 2.01/05/2026 - Diesel tank cleaned
| DG Set - 3 (15 KVA) | Cummins | Model : 8061332 SR No :H10I074598 | 06/06/2025 | 2026-06-02 | 1. Main alternator need to be service 2. Air filter need to be replace
GTC 50-03 | Carrier engine | CAT | Model : C-3 SR No : RRA17724 |  | 25/04/2026 | 1. Commissioning completed by GMMCO
| Mud pump engine | Cummins | Model : KTA19-C600 SR No : 41398853 |  | 26/05/2026 | 1. Commissioning completed by Cummins
| DG Set - 1 (125 KVA) | ASHOK LEYLAND | Model : H6G4DE125 SR No : TPHM108062 |  | 22/05/2026 | 1. Commissioning completed by Cummins
| DG Set - 2 (125 KVA) | ASHOK LEYLAND | Model : H6G4DE125 SR No : TPHM107062 |  | 22/05/2026 | 1. Commissioning completed by Cummins
GTC 100-02 | Carrier engine | CAT | Model : C-15 SR No : JDK00370 | 09/11/2025 | 05/01/2026 | 1. Coolant level sensor not working 2. 18/12/2025 - Engine timing cover gasket leaks. 3. 5/1/26 - turbo lube oil supply line need to replace. | 1. MP & RC Coolant sensor Pending. 2. 24/1/2026 -Timing gasket & front seal fitetd tested and found ok. 3. Ask confirm with mili engine ok no need for oil lubricating line.
| Mud Pump engine | Cummins | Model : KTA-1150-C SR No : 25372916 | 29/01/2025 | 24/06/2025 | 1. Replace all coolant line hoses 2. Require fuel filter housing 3. Fuel return line hose 4.Engine wiring harness 5. Lube oil pre. Gauge 6. Magnetic switch 1 nos 7. Accessories drive belt | 1. 03/07/2025 - Discussed with Mr. Mili regarding the health check-up. We need to work on all the following points to prevent future maintenance issues 2. 04/07/2025 - MR has been raised against each point. 3. Revised quotation Received from the Vendor
| DG Set - 1 (125 KVA) | Cummins | Model : 6BTAA59-G3 SR No : 84012589 | 24/06/2025 | 21/02/2026 | 1. Need to replace realy control module 2. Need to replace engine wiring harness 3. Change upper engine gasket 4.Replce or repair charging alternator 5. Lift pump 6. Turbo charger need to replace 7. Head gasket need to be replace 8.Battery alternator need to be repair | 1.07/02/2026 - Long block installation done turbo,relay,fuel transfer pump replaced. 2.21/02/2026 - Relay & Engine harness replaced 3.30/04/2026 - Alternator repaired tested & found ok
| DG Set - 2 (125 KVA) | Cummins | Model : 6BTAA39-G3 SR No : 84012584 | 24/06/2025 | 21/02/2026 | 1. Need to replace realy control modual 2. Change upper engine gasket 3. PSO 500 conversion PSO 600 4. tensioner belt 5. Lift pump 6.Battery alternator need to be repair | 1.09/03/2026 - Oil seal,relay,controller,changed. 2.30/04/2026 - Alternator repaired tested & found ok
| DG Set - 3 (25KVA) | ASHOK LEYLAND | Model : AL485TADG3 SR No : BB12215973 | 28/01/2026 | 06/02/2026 | 1.Fan belt need to be replace 2.Water temperature sensor and switch need to be replaced | 1.28/01/2026 - Engine overhauling, part fiting Wiring harness,solenod switch turbo,thermostat,hosepipe,mounting,head gasket mounting,radiator replaced. 2.06/02/2026 - Fan belt,Temperature sensor, Temperature switch replaced.
GTC 100-03 | RIG CARREIR ENGINE | CAT | Model : C-15 SR No : JDY00701 | 23/07/2025 | 11/11/2025 | 1. Atmospheric Sensor to be Changed 2. Boost pressure Sensor to be Changed | 1. 11/11/2025- Atmospheric Sensor has been Replaced 2. 11/11/2025- Boost pressure Sensor Problem solved
| MUD PUMP | CUMMINS | Model : VTA-28-P ENGINE NO- 25386955 SR No : 35294 | 10/06/2025 | Mar-2026 | 1. Hoses and clampe need replace 2. RPM meter 3. Lub oil pressure gauge 4. Coolant temperature gauge 5. Lub oil temperature gauge | 1. All the point have been rectified & resolved (Replaced a RPM meter)
| DG Set - 1 (125 KVA) | SUPERNOVA | Model : EE694TCI SR No : E622CDKE287046G | 22/07/2025 | 16/04/2026 | 1. DG Radiator service Required. 2. Fuel Tank Cleaning Required. 3. Fuel Suction hose pipe Required to Replace. 4. Feed pump/Hand primmer Need to Replace. 5. DG Stop Solenoid Need to Replace. 6. Customer need to use Supernova Company Genius spares for DG service. | 1. 23/04/2026- Cleaned Radiator 2. 24/04/2026- Fuel Tank Cleaned 3. 19/06/2026- pending materials will receive today at duliyajan office
| DG Set - 2 (125 KVA) | SUPERNOVA | MODEL : EE694TCI SR No : E622CDKE286872G | 22/07/2025 | 16/04/2026 | 1. Radiator Cleaning/Servicing Required. 2. Fuel Tank Cleaning Required. 3. Stop Solenoid Need to Replace. 4. Fuel Suction hose pipe need to Replace. 5. Fuel Primming pump.( Hand Primmer) Need to Replace. 6. Advice to customer use Supernova Company Genius spares for DG Service. | 1. 24/04/2026- Cleaned Radiator 2. 23/04/2026- Fuel Tank Cleaned 3. 19/06/2026- pending materials will receive today at duliyajan office
| DG Set - 3 (25 KVA) | ASHOK LEYLAND | MODEL : AL2CTIDG2 SR No : PRHM123709 | 23/04/2025 | 12/11/2025 | 1. Rectifier issue | Alternator repaired tested & found ok
GTC 100-04 | Carrier engine | Caterpillar | Model : C-15 SR No : JDY00759 | 23/07/2025 | 11/11/2025 | 1. Harness found Damaged | 1. 11/11/2025- Harness Problem Solved
| Mud Pump engine | Caterpillar | Model : C-15 SR No : MCW08600 | 23/07/2025 | 11/11/2025 | 1. Coolant Sensor to be Changed | 1.11/11/2025- MP Coolant Sensor Changed
| DG Set - 1 (125 KVA) | Cummins | Model : 6BTAA5. 9G13 SR No : P84234616 | 3/12/2025 | 11/04/2026 | 1. Cooling System hoses found hard 2. Radiator Chocked 3. fuel Leakage from fuel pump 4. Need to Change 12V Reley | 1. 20/06/2026- Radiator Cleaned
| DG Set - 2 (125 KVA) | Cummins | Model : 6BTAA5.9-G13 SR No : P84234524 | 11/04/2026 | 17/06/2026 | 1. Observed Leakage from head gasket, need to replaced a head gasket | 1. 19/06/2026 - Quotation already shared with Suraj 2. 20/06/2026 - Service Engineer will visit in next week to close out point
| DG Set - 3 (15KVA) | Ashok Leyland | Model : H2G4DM15 SR No : RDHM120144 | 17/07/2024 (NEW) | 22/07/2025 | 1. Lub Oil level low, need to Top up | 1. Engine oil top up as per Requirment.
GTC 100-07 | Carrier engine | CAT | Model : C-15 SR No : MCW10973 | 20/07/2025 | 12/11/2025 | 1. Coolant sensor not working | 1. RC Coolant sensor Pending
| Mud Pump engine | CAT | Model : C-15 ( LGF-500 ) SR No : MG200154 | 08/05/2025 | 20/07/2025 | 1. Throttle Position Error code. 2. Water pump Issue 3. 08/04/2026 - Oil level increase automatically | 1. Next Health Check-up is planned on Jan - 2026 2.10/01/2026 - Water pump fittd tested & Found ok. 3. Diagnosis in progress by mili & MIC
| DG Set - 1 (125 KVA) | ASHOK LEYLAND | Model : AL6DTIDG2 SR No : ETHM421188 | 07/07/2025 | 27/04/2026 | 1. Radiator need to be clean 2.Fuel meter unit, fuel strainer, oil cap need to be replace | 1. Radiator external cleaned.
| DG Set - 2 (125 KVA) | ASHOK LEYLAND | Model : AL6DTIDG2 SR No : ESHM422840 | 10/10/2025 (Overhauling) | 27/04/2026 | 1.Radiator need to be clean. 2. Temperature sensor,LOP sensor,diesel pipe,wiring harnessfuel meter unit need to be replace. | 1. Radiator external cleaned. | 10/10/2025 (Overhauling)
| DG Set - 3 (30KVA) | Supernova | Model : EE483TCI SR No : E412CDJJ235425G | 25/01/2025 | 17/08/2025 | 1. Controller not working 2. Expansion bellow need to replace 3. Air filter need to replace | MR raised
GTC 100-08 | Carrier engine | CAT | Model : C-15 SR No : MCW20163 |  | 05/01/2026 |  | 1. 05/01/2026 - Commissioning was completed by CAT authorized Vendor (GAINWELL) | New Carrier Engine
| Mud pump engine | CAT | Model : C-27 SR No : TWM02440 | 20/07/2025 | 12/11/2025 | 1.Coolant level sensor not working 2. Alternator send for repairing
| DG Set - 1 (125 KVA) | ASHOK LEYLAND | Model : AL6DTIDG2 SR No : FYHM412850 | 19/12/2025 | 28/01/2026 | 1.Oil sensor to be changed 2.Fuel meter unit 3.Fuel stainer 4.Wiring connector 5.Benjo boult and washer 4pcs 6.Charging alternator nto be check | 1.19/12/2025 - Controller, relay, diode plate,armature changed,engine tested and found ok. 2. Next Health Check-up is planned on June - 2026
| DG Set - 2 (125 KVA) | ASHOK LEYLAND | Model : AL6DTIDG2 SR No : EFHM425790 | 26/06/2025 | 19/12/2025 | 1. Engine oil,oil filter,air,fuel filter need to be replace. 2. Relay need to be change. 3. controller need to be change. 4. Excuator need to be change. 5. Diesel pipe,battery terminal,oil sensor,thermostat need to be change. 6. Wiring harness need to check & Repair. | 1. 19/12/2025 - Ameature controller change, Relay replaced 2. 12/01/2026 - Wiring harness changed,Controller,actuator,oil sensor,Diesel pipe, relay, Engine service done. 3. 12/01/2026 - Tested and found Ok. 4. Next Health Check-up is planned on June - 2026
| DG Set - 3 (25 KVA) | ASHOK LEYLAND | Model : AL2CTIDG 2 SR No : NLHM103612 | 26/06/2025 | 28/01/2026 | 1.Governor actuator not working properly. 2.AVR,Radiator mounting,raditor service tappet gasket,thermostat,actuator link rod,FIP pump rpm spring replace recommended | 1. 23/10/2025- Water Pump Damaged 2. 24/10/2025- Water Pump Replaced, found Ok 3. Next Health Check-up is planned on June - 2026
GTC 160-01 | Carrier engine | CAT | Model : C-18 SR No : WRH16390 |  | 06/04/2026 | 1. Commissioning completed by Gainwell
| Mud pump engine | Cummins | Model : KTA19-C600 SR No : 41398852 |  | 02/05/2026 | 1. Commissioning completed by cummins
| DG Set - 1 (125 KVA) | Cummins | Model : QSB4.5-G2 SR No : 62B95560043 |  | 02/05/2026 | 1. Commissioning completed by cummins
| DG Set - 2 (125 KVA) | Cummins | Model : QSB4.5-G2 SR No : 62B95556019 |  | 02/05/2026 | 1. Commissioning completed by cummins
| DG Set - 3 (40 KVA) | Cummins |  |  | 19/04/2026 | 1. Commissioning completed by cummins
GTC 150-02 | Carrier engine -1 | CAT | Model : C-15 SR No : JRE04222 | 23/12/2025 | 16/01/2026 | 1. oil leakage from timing cover gasket | 1.07/05/2026 - Akram bhai visited and fixed chamber gasket concerned solved.
| Carrier engine -2 | CAT | Model : C-15 SR No : JRE06832 | 23/12/2025 | 16/01/2026 | 1.Oil leakage from oil sump bolt | 1.23/12/25 - MR raised against concern. 2. 22/04/2026 - Timing side gasket replaced concrern solved
| Mudpump Engine - 1 | CAT | Model : C- 27 SR No : TWM02896 | 09/01/2026 | 07/05/2026 | 1. Engine tested and found ok
| Mudpump Engine - 2 | CAT | Model : C- 27 SR No : TWM02886 | 09/01/2026 | 07/05/2026 | 1.Resistance need to be change | 1. 10/05/2026 - Resisitance change and found ok.
| DG set -1 (500 KVA) | CAT | Model : C-15 SR No : FTH05469 | 09/01/2026 | 08/05/2026 | 1. Head change done 2. 26/06/2025 - ALL Sensor MR Raised 3. All the Sensor Installed in Engine expect Coolant level sensor 4. 09/07/2025 - Received Engine from Bakrol yard. 5. fan Assembly, fan belt pully & fuel line replaced from CAT DG-1 & Installed on CAT DG-2. 6. 09/01/2026 - old fan fitted and diesel line leaks 7. 12/01/2026 - Fan assembly fitted 8. 25/04/2026 - oil seal leak from flywheel side 9. Oil spilling from turbo | 1. 16/07/2025 - Received from 200-01 2. 17/07/2025 - Engine Dismantled by ICPS Engineer 3. 21/08/2025- Engine Sent to ICPS 4. 29/08/2025 - will take atleast 15 days for Repairing 5. 5/10/2025 - Overhauled Engine Received at yard 6. fan pulley need to replaced/PO under approval 7. new fan will received from 200-1 and diesel line fitted from another D.G by paresh bhai. 8. 12/01/2026 - Fan assembly tested and found ok. 9. 21/05/2026 - Injector and turbo send to vendor for calibraton, Turbo ok
| DG set -2 (500 KVA) | CAT | Model : C-15 SR No : FTH05473 | 09/01/2026 | 08/05/2026 | 1. fan Assembly, fan belt pully & fuel line replaced from CAT DG-1 & Installed on CAT DG-2. 2. 09/01/2026 - old fan fitted and diesel line leaks 3. 12/01/2026 - Fan assembly fitted 4. 09/04/2026 - Engine at akram bhai workshopfor major over hauling head found crack/Turbo need to replace , chmaber damaged | 1. fan pulley need to replaced/PO under approval 2. new fan will received from 200-1 and diesel line fitted from another D.G by paresh bhai. 3. 12/01/2026 - Fan assembly tested and found ok. 4. 25/04/2026 - Top overhauled by akrambhai, turbo core replaced, fuel pump and injector calibrate | Overhauled in april by akram bhai
| DG Set-3 (125 KVA) | Supernova | Model: EE694TCI - 125 KVA SR.No: E622CDJE214975G | 27/03/2026 | 16/04/2026 | 1. Charging alternator 2. Panel Wiring 3. Start stop relay 4.Diesel inlet & outlet pipe 5. Actuator (Solenoid) 15/04/2026 - Fuel and oil mix in oil sump | 1. Alternator repaired, Panel wiring repaired 2.17/04/2026 - Fuel pump & Injector sent to vendor for calibration.
| DG Set-4 (62.5 KVA) | Supernova
GTC 200-01 | Carrier engine - 1 | CAT | Model : C-18 SR No : WRH01405 | 29/12/2025 | 02/01/2026 | 1. According to health Check-Up, there is no fault in Engine
| Carrier engine - 2 | CAT | Model : C-18 SR No : WJW00271 | 14/07/2025 | 02/12/2025 | 1. According to health Check-Up, there is no fault in Engine | 1. Next Health Check-up is planned on Mar - 2026
| Mud Pump engine -1 | CAT | Model : C-32 SR No : TLD01455 | 28/05/2025 | 02/12/2025 | 1. According to health Check-Up, there is no fault in Engine 2. 09/01/2026 - Oil cooler choked. | 1. Next Health Check-up is planned on Mar - 2026 2. 13/01/2026 - oil cooler fitted tested & found ok.
| Mud Pump engine -2 | CAT | Model : C-32 SR No : TLD01456 | 02/12/2025 | 25/12/25 (Overhauled by Akram) | 1. Top overhauling done by akram bhai - (DEC- 2025) 2.26/01/02026 - oil consumption high 3.23/06/2026 - Turbo become red hot | 1. Top over hauling done but engine consume oil. 2. 25/12/25 - Piston ring new fitted. 3. ECM replaced and injector also replaced | 25/12/25 (Overhauled by Akram)
| DG Set -1 (500 KVA) | CAT-1 | Model : C-15 SR No : FTH05473 | 14/07/2025 | 20/08/2025 | 1. According to health Check-Up, there is no fault in Engine. 2. Water pump need to replace due to over heat issue. 3. 14/12/2025 - Injector faulty | 1. Next Health Check-up is planned on Jan - 2026 2. Water pump impellar size is small so sent back to yard. 3. 13/01/2026 - Fitted and found ok
| DG Set -3 (500 KVA) | CUMMINS-DG-1 | MAKE/Model : KTA-19-G9 SR No : 25735818 | 06/06/2025 | Sep - 2025 (Overhauled by Akram) | 1. Top Overhauling done by akrambhai on Sep-2025 2. water pump leaks 3. 15/12/25 - Fuel line leaks 4. Front & Rear seal leaks 5. 1/1/26 - front & Rear seals leaks 6. 5/1/2026 - Fan belt need to replace. 7. Radiator need to be repair. 8.27/04/2026 - rear oil seal leaks 9.23/06/2026 - coolant from turbo spills | 1. Working ok 2. 10.12.25 - Water pump replaced tested and found ok. 3. 15/12/25 - Fuel line repairing done,check & found ok. 4. 25/12/25 - Front & Rear seal fitted tested and found ok. 5. 5/1/2026- Seal fitment done tested and fond ok. 6. 5/1/2026 - MR raise against point. 7. Radiator service done tested and found ok. 8. Will be repaired in ILM 9.24/06/2026 - Cylinder liner change | Sep - 2025 (Overhauled by Akram)
| DG Set -4 (500 KVA) | CUMMINS-DG-2 | MAKE/Model : KTA-19-G9 SR No : 25735817 | 11/12/2025 | 22/05/2026 (Overhauled by karnavati) | 1. 11/12/25 - MPU need to be replace. 2. 15.12.25 - Fuel pump need to be calibrate 3. 15.12.25 - PT-pump governor stuck problem. Rectified by Cummins eng 4. 24/01/26 - PCB need to repair 5. 10/04/2026 - Controller button not working 6. 15/05/2026 - Oil spill out from exhaust manifold | 1. 14/12/2025 - MPU has been replace. 2. 19/12/2025 - Fuel pump sent to vendor for callibration. 3. 26/12/2025 - Fuel pump fitted tested and found ok. 4. 10/04/2026 - PCB replaced tested and found ok. 5. 10/04/2026 - MR placed for controller button. 6. 22/05/2026 - DG installed at site tested & found ok | Top overhauled at karnavati in MAY
| DG Set -5 (125 KVA) | SUPERNOVA | Model : EE694TCI SR No : E622CDKE214975G | 23/01/2025 | 19/12/25 | 1. According to health Check-Up, there is no fault in Engine. 2. Air Filter need to be change. 9/2/2026 - Head gasket leaks | 1. Air filter changed 2. As per confirmation with ompuri no oil leaks
| D.G Set -6 (62.5 KVA) | SUPERNOVA | Model: SWE7 SR.No: SEL SWE7P9-718-318 |  |  | 1. Fuel filter line to be change 2. Diesel line to be change. | 1. MR raised against point
GTC 250-01 | Carrier engine | CAT | Model : C-18 SR No : WJY00647 | 26/12/2024 | 17/06/2025 | 1. According to health Check-Up, there is no fault in Engine
| Carrier engine | CAT | Model : C-18 SR No : WJY00653 | 26/12/2024 | 17/06/2025 | 1. According to health Check-Up, there is no fault in Engine
| Mud Pump -1 (engine -1) | CAT | Model : C-18 SR No : WJH02772 | 26/12/2024 | 22/01/2026 | 1) Fuel mechanical priming pump defective - Need replacement 2) Fuel relief valve low pressure- Repair/Replace 3) Injectors of fuel system need test bench analysis 4) Safety bypass valve check required 5) CAM and Crank position sensors check required | 1.24/01/2026 - Injector & fuel pump sent to vendor. 2.25/02/2026 - Fuel Pump & Injector feed pump and fuel sensor fitted tested & found faulty.
| Mud Pump -1 (engine -2) | CAT | Model : C-18 SR No : WJH02761 | 26/12/2024 |  | 1. According to health Check-Up, there is no fault in Engine | 1. Engine Was not available at the time of Health Check-up
| Mud Pump -2 (engine -1) | CAT | Model : C-18 SR No : WJH02737 | 11/03/2025 | 20/06/2025 | 1. According to health Check-Up, there is no fault in Engine
| Mud Pump -2 (engine -2) | CAT | Model : C-18 SR No : WJH02749 | 26/12/2024 | 20/06/2025 | 1. According to health Check-Up, there is no fault in Engine
| DG Set - 1 (320 KVA) | Cummins | Model : NTA-855-G2-I SR No : 25395018 | 27/05/2025 | 25/11/25 | 1. Radiator internal choked | 1. 15/1/2026 - Radiator fitment done tested and found ok.
| DG Set - 2 (320 KVA) | Cummins | Model : NTA-855-G2-I SR No : 25395024 |  | 25/11/25 | 1. 07/05/2026 - oil and water mix | 1. Overhauling in progress.
| DG Set - 3 (320 KVA) | Cummins | Model : NTA-855-G2-I SR No : 25395075 | 04/02/2025 | 10/05/2026 | 10/05/2026 - DG overhauled at Rajamundry | 1. 14/05/2026 - DG overhauled tested and found ok | Top Overhauled in May by local mechanic
| DG Set - 4 (63 KVA) | Ashok Leyland | MODEL : AL4CTIDG2 SR No : MDHM110040 | 02/07/2025 | 28/05/2026 | 28/05/2026 - DG overhauled at Rajamundry | 1. 28/05/2026 - DG overhauled tested and found ok | Top Overhauled in May by local mechanic
| DG Set - 5 (15 KVA) | Ashok Leyland | MODEL: AL485G1 SR No : BB11215392 |  | 02/07/2025 | 1. Expansion bellow cracked 2. Suction fuel pipe small filter need to be replaced 3. mounting not properly with earth surface rubber mats | 1. All the point have been rectified & resolved ( Expansion bellow Repaired, Cleaned Suction fuel small filter, mounting done )
GTC 1000-01 | Carrier engine -1 | CAT | Model : C-18 SR No : WJW00272 | 14/07/2025 | 13/01/2026 | 1. Coolant Sensor Error Code 2. 08/01/2026 - Emitts black smoke from engine. 3. 17/01/2026 - Intercooler,oil cooler and radiator choked. Sending to vendor k.Tech. | 13/01/2026 - 1) Fan direction changed, Radiator serviced. Accelator throttle serviced and installed. 2. 24/01/2026 - Intercooler, Radiator,oil cooler fitted.
| Carrier engine -2 | CAT | Model : C-18 SR No : WRH11041 | 02/12/2025 | 08/01/2026 (Overhauled by Akram) | 1.Top Overhauling done by akrambhai on Jan-2026. 2. 10/01/2026 - Cylinder Liner to be install new as water leaks 3. 14/01/2026 - Engine emitts black smoke. 4. 15/01/2026 - oil cooler damage need to repair. 5. 25/02/2026 - Oil and coolant mixing | 13/01/2026 - 1) Water pump replaced and tested ok. 2) Radiator washing done. 3)Fan direction changed. 4)Ignition switch replaced by new one. 5) Changed air filter. 14/01/2026 - 1. Oil cooler change. 26/02/2026 - Sent at akram bhai workshop | 08/01/2026 (Overhauled by Akram)
| Mud Pump engine -1 | Cummins | Model : KAT38-C1300 SR No : 41284958 | 13/06/2025 | 17/12/2025 (Overhauled by Akram) | 1. Top overhauling done by akrambhai on Dec - 2025. 2. 18/12/2025 - Fuel Leaks | 1. 17/12/2025 - Over hauling done ,Working ok. 2. 18/12/2025 - Fuel leak concern solved. 3. Next Health Check-up is planned on June - 2026 | 17/12/2025 (Overhauled by Akram)
| Mud Pump engine -2 | Cummins | Model : KAT38-C1300 SR No : 41284957 | 03/01/2026 | 26/01/2026 (Overhauled by Karnavati) | 1. 26/01/2026 - received from karnavati major overhauling done, all filter change, Radiator, oilcooler, intercooler service done. 2. 03/02/2026 - service done, injector calibration done, head gasket change, connecting rod changed. | 1. Next Health Check-up is planned on June - 2026 | 26/01/2026 (Overhauled by Karnavati)
| DG Set - 1 (500 KVA) | Supernova | Model : 2506D-E15TAG2 SR No : MGBF8088S00423E | 2025-06-12 | 26/03/2026 | 1) oil sump gasket need to replace 2) Tappet cover Gasket need to replace 3) Fuel pump Gasket need to replace 4) Secondary fuel filter body ( Bowle) need to replace 5) Turbocharger Return line pipe O'Ring need to replace 6) Coolant line Hoses with clamp need to replace 7) Air intek line hoses with clamp need to replace 8) Fan belt and Alternator belt need to replace 9) Engine Is required major overhaul as per service protocols. | 1. 27/03/2026 - Overhauling Inspection completed by Supernova
| DG Set -2 (500 KVA) | Supernova | Model : 2506D-E15TAG2 SR No : MGBF8088S00237D | 2025-12-06 | 26/03/2026 | 1)Fuel feed pump need to replace 2)oil sump gasket need to replace 3)Front side timing cover Gasket need to replace 4)Fan belt and Alternator belt need to replace 5)Coolant line Hoses with clamp need to replace 6)Air intek line Hoses with clamp need to replace 7)Cylinder Head Gasket leckage need to replace 8) Water pump seal found leckage need to Replace water pump 9) This DG is Required major overhaul as per service protocols. 10) Diesel filter & Coolant temperature switch need to be replace | 1. 27/03/2026 - Overhauling Inspection completed by Supernova
| DG Set - 3 (500 KVA) | Supernova | Model : 2506D-E15TAG2 SR No : MGBF8088S00238D | 30/10/2025 (Overhauled by Akram) | 18/05/2026 | Required Overhauling 1. Exhaust Gasket Leaks 2. Excess fuel consuption 3. 6/1/2026 - Radiator Leaks 7/2/2026 - Exhaust manifold over heats,fuel filter leaks 4. Fuel injector & Radiator send for service 5. 15/05/2026 - Turbo become red hot and trips 6. 28/05/2026 - Supernova engineer visited tested & Found ok. Also need to replace oil sump, timing side gasket and injector wiring. | 1 . 11/12/2025 - Exhaust manifold gasket replaced tested and found ok,excess fuel consumption concern under observation. 2. 2/1/2026 - Fuel consumption rate normal. Concern solved. 3. 8/1/2026 - Radiator Service done tested and found on 4. 12.02.2026 - Injector send at advance for calibration. 5.14/02/2026 - Injector fitment done Service engineer will visit with ET tool. 6. Supernova engineer visited injector need to be service. 7. 22/05/2026 - Injector replaced still trips 8. 28/05/2026 - Supernova engineer visited tested & Found ok | 30/10/2025 (Overhauled by Akram)
| D.G Set -4 (125 KVA) | Supernova | Model: EE694TCI - 125 KVA Sr.No: E622CDHL175515G | 12-06-2025 | 6/12/2025 | 1. 10/2/2026 - Fuel and coolant mix | 1.14/02/2026 - O - ring replaced tested & found ok
GTC 1000-02 | Carrier engine - 01 | CAT | Model : C-15 MAX-1500M ALT 4922 FT SR No : JRE03930 | 28/12/2024 |  | 1. According to health Check-Up, there is no fault in Engine | 1. Contract has been Completed
| Carrier engine - 02 | CAT | Model : C-15 MAX 1500M ALT 4922 FT SR No : JRE04440 | 28/12/2024 |  | 1. According to health Check-Up, there is no fault in Engine | 1. Contract has been Completed
| Mud Pump engine - 01 | CAT | Model : C-27 Engine Family : ACPXL270ESX SR No : TWM02886 | 28/12/2024 |  | 1. According to health Check-Up, there is no fault in Engine | 1. Contract has been Completed
| Mud Pump engine - 02 | Detroit | Model : Detroit Model : 12V-71TI ENGINE No : 12VA 89517 |  |  | 1. According to Purchase department, The Health check-up has not been done yet | 1. Contract has been Completed
| DG Set - 1 (320 KVA) | Cummins | Model : NTA-855-G2-I ENGINE No : 25394946 | 03/08/2024 |  | 1. 23/11/2025 - The Work order was Sent to the Vendor, But Vendor Advised that a health check-up is not required because the entire Engine was repaired in December | 1. All the point have been rectified & resolved ( DG successfully service done. ) 2.Contract has been Completed.
| DG Set - 2 (320 KVA) | Bourdain | Model : 6M16G4D2/5 SR No : 4923D002047 | 23/04/2025 |  | 1. RPM Problem | 1. All the point have been rectified & resolved ( RPM Problem Resolved by RAMP) 2. Contract has been Completed
| DG Set - 3 (160 KVA) | SUPERNOVA | Model : EF694TCI SR No : E622CDKE288054G | 24/01/2025 |  | 1. Rocker arm cover need to be replaced 2. B Check need to be done Immediately 3. Coolant need to be replaced 4. Required Engine radiator servicing 5. Fan Belt to be Replaced | 1. All the point have been rectified & resolved (Repaired Rocker arm cover, B Check-up has been Completed, Replaced a Coolant, Replaced a Radiator, Replaced a fan Belt ) 2. Contract has been Completed
| DG Set - 4 (30 KVA) | SUPERNOVA | Model : EE483TCI SR No : E412CDKE203915G | 24/01/2025 |  | 1. Health Check-up were Conducted for DG-3 and DG-4 at the Same time, but the Supernova Vendor has not yet sent the health Check-up report for DG-4 2. 30/05/2025 - Asked for the health check-up report to Supernova Vendor, but still haven't got it. | 1. We have been following up with the Supernova vendor, but didn't get the report yet.

## Transmission Health Check up
HEALTH CHECK - UP
Rig | Transmission Application | Transmission Make | Transmission Details | Previous Health Check-up | Last Health Check -up | Problem | ACTION | Status
GTC 50-01 | Carrier engine Transmission | Allison | Model : 08K-28TIDA SR No : 6620008308
| Mudpump engine Transmission | Allison | Model : S6610H SR No : 3110113593 |  | 08/01/2026 | 1. Transmission Tested & found Ok
GTC 50-02 | Carrier engine Transmission | Allison | Model : 08K-28TIDA SR No : 6620008307
| Mud Pump engine Transmission | Allison | Model : CLBT-6061 SR No : 31601300 |  | 10/01/2026 | 1. Transmission temperature found high as like 104-to-105-degree Celsius. 2. Required Complete Service of Transmission for gear shifting issue, low pressure & high temperature.
GTC 100-02 | Carrier engine Transmission | Allison | Model : S6610HR SR No : 311011457 |  | 27/04/2026 | 1. Transmission Tested & found Ok
GTC 100-03 | Carrier engine Transmission | Allison | Model : M5620AR SR No : 3110118997 |  | 02/05/2026 | 1. found Oil Pressure Low, Required 190-220 PSI
| Mud Pump engine Transmission | Allison | Model : CLBT5860-4 SR No : 728657013 |  | 02/05/2026 | 1. Transmission Tested & found Ok
| Cementing Pump engine Transmission | Allison | Model : CLBT754 SR No : 2510067968 |  | 02/05/2026 | 1. Transmission Tested & found Ok
GTC 100-04 | Carrier engine Transmission | Allison | Model : M5620AR SR No : 3110119121 |  | 28/04/2026 | 1. Transmission Tested & found Ok
| Mud Pump engine Transmission | Allison | Model : CLBT6061-4 SR No : 6836233 |  | 28/04/2026 | 1. Output Oil Seal Leakage | 1. 02/05/2026- Replaced Oil Seal by Bharat Transmission Technician
GTC 100-07 | Carrier engine Transmission | Allison | Model : S6610HR SR No : 3110111458 |  | 28/04/2026 | 1. Transmission Tested & found Ok
| Mud Pump engine Transmission | Allison | Model : CLBT 6061 SR No : 31601371 |  | 28/04/2026 | 1. Transmission Tested & found Ok
GTC 100-08 | Carrier engine Transmission | Allison | Model : 4870OFS SR No : 6620057758 |  | 27/04/2026 | 1. Transmission Tested & found Ok
| Mud Pump engine Transmission | Allison | Model : S6620H SR No : 3110115261 |  | 27/04/2026 | 1. Transmission Tested & found Ok
GTC 150-02 | Carrier engine -1 Transmission | Allison | Model : M5610AR SR No : 3110114634 |  | 11/01/2026 | 1. Transmission Tested & found Ok
| Carrier engine -2 Transmission | Allison | Model : 56200FS SR No : 3110121480 |  | 11/01/2026 | 1. Transmission Tested & found Ok
| Mud Pump engine -1 Transmission | Allison | Model : S6620H SR No : 3110115943 |  | 07/06/2026 | 1. Transmission replaced & Tested found ok
| Mud Pump engine -2 Transmission | Allison | Model : S6620H SR No : 3110115942
GTC 200-01 | Carrier engine -1 Transmission | Allison | Model : 66200FS SR No : 3110121450 |  | 08/01/2026 | 1. Transmission Tested & found Ok
| Carrier engine -2 Transmission | Allison | Model : M6610A SR No : 31602555 |  | 17/04/2026 | 1. Transmission Oil Colour found Brown. 2. Need to Change Oil & Oil filter 3. Transmission replaced & Tested found ok
| Mud Pump engine -1 Transmission | Power Trans | Model : DP8961 SR No : 4310003529 |  | 08/01/2026 | 1. Transmission Tested & found Ok
| Mud Pump engine -2 Transmission | Allison | Model : H8610A SR No : 4310009797 |  | 08/01/2026 | 1. Transmission Tested & found Ok
GTC 1000-01 | Carrier engine -1 Transmission | Allison | Model : S6620HR SR No : 3110116193 |  | 09/01/2026 | 1. Transmission Tested & found Ok
| Carrier engine -2 Transmission | Allison | Model : 66200FS SR No : 3110121447 |  | 12/01/2026 | 1. Gear Shifting not working properly 2. Required Control Valve Servicing | 1. Pareshbhai replaced Mechanical Control valve with Electrical one on 13.01.2026. Now, Gear shifting working properly
| Mud Pump engine -1 Transmission | Guizhou Vinstar | Model : BY2060 SR No : KX18239 |  | 09/01/2026 | 1. Transmission Oil colour found very black. As discussed with Idrish bhai, this could be due to clutch failure. 2. Required Complete Service of Transmission
| Mud Pump engine -2 Transmission | Power Trans | Model : DP8962-4 SR No : 4310006388 |  | 09/01/2026 | 1. Transmission Tested & found Ok

## Bakrol & Central Store
Rig | Engine Application | Engine Make | Engine Details | Date | Problem | ACTION | Remarks | Place
50-02 | Carrier engine | CAT | Model : C-9 SR No : JSC08780 | 24/05/2025 | 1. Found Cooler hose damaged 2. Air boost Pressure Not found ok 3. Cooler hose shrinkage, Then check other lube air hose damaged 4. Need to be replace other straight air hose | 1. 27/05/2025 - Replaced a Cooler hose 2. 27/05/2025 - Replaced a Turbo Charger 3. 27/05/2025 - Replaced Air Inlet hose 4. 27/06/2025 - Rocker art shaft bolt MR raised | 1. Dismantle of Engine was Completed at 44000 hrs (30/05/2025) 2. Engineer taken Some Pictures of parts to discuss with his manager 3. All the Parts Should be properly Wrapped. | Akram workshop
150-02 | Carrier engine (Original) | CAT | Model : C-15 SR No : MCW13178 |  |  |  |  | Assam
1000-1 | Carrier engine -2 | CAT | Model : C-18 SR No : WRH10662 | 12/08/2025 | 09/01/2026 | 1. Water containment in oil | 1. 07/04/2026 - Overhauling Completed & Tested founf OK | Central Store
100-01 | Carrier engine | CAT | Model : C-15 SR No : JDK00371 | 20/07/2025 | 06/11/2025 | 1. 03/01/2026 - Engine at ICPS for top overhauling. 2. Overhauled Engine Received at Bakrol Yard |  | Bakrol Yard
150-02 | Mud Pump engine | CAT | Model : C-15 SR No : JDY00657 |  |  | 1. The Health check-up has not been done yet, Paresh Patel will be visiting soon. | 1. Discussed with Paresh Patel regarding health Check-up, but he is not able to give me a date. | Bakrol Yard
| DG Set - 1 (62 KVA) | Supernova | Model : EE483TCI SR No : E412CDNM417212G | 08/01/2026 | 21/01/2026 | 1. Stop solenoid not working 2. fan belt need to replace 3. Required Radiator Cleaning 4. Water & oil mix 5. oil cooler new required | 1. 26/02/2026 - Radiator service done new intercooler fitted manually operation found ok, electrical work to be done | Bakrol Yard
| DG Set - 2 (125 KVA) | Supernova | Model : EE694TCI SR No : E622CDHL175292G | 13/10/2025 | 08/01/2026 | 1. Engine service Due so engine service required 2.Coolant Replacement Required 3.fan belt Required 4.F.I. Pump & Nozzal Service & Repairing Required 5.Tappet Setting Required. 6.Oil pressure Switch Required 7.Coolant Temp. Switch required. 8.Panel & Engine wiring Repairing Required. 9.AVM Pad Required 4 Nos. 10.after work Complete Engine perfomance check required | 1. 09/01/2026 - Quotation Pending from Vendor | Bakrol Yard
| DG Set - 3 (125 KVA) | Supernova | Model : EE694TCI SR No : E622CDJD208499G | 27/04/2025 | 13/10/2025 | 1. controller programming software issue 2. DG Alternator not working 3. Required Radiator Cleaning 4. Oil Pressure Sensor not Working | 1. 13/10/2025- Software Updated in Controller 2. 13/10/2025 - Wiring harness tighten & Cleaned. DG Alternator tested ok | Bakrol Yard
| DG set -4 (62.5 KVA) | Supernova | Model : EE483TCI SR No : E412CDJD207865G | 13/10/2025 (Major Hauling) | 08/01/2026 | 1. Engine service required 2. stop Solenoid required 3.Panel & Engine wiring Repairing Required 4.Avm pad required 4 No. 5.Rediater Cowl required 6.exhaust bellow with Gasket required 7.Rediater fan required | 1. 13/2/2026 - spare received at yard fitment in process 2. 16/2/2026 - AVM pad, radiator fan exhaust bellow fitted,tested and found ok. | Bakrol Yard
| DG Set - 5 (30 KVA) | Supernova | Model : EE483TCI SR No : E412CDHL176899G | 13/10/2025 | 21/01/2026 | 1.Rediater Service Required 2.Oil Cooler Replacement Required 3.AVM Pad Damaged So AVM Pad Required 4.Exhaust bellow Required 5.Relay 12V 4pin 40A Required | 1. Quotation pending from vendor | Bakrol Yard